Internal memo no. 912/177  - const division					Date: 19-11-2025

Subject: clarification on fire extinguishers.

Keywords: fire extinguishers, CO2, ABC,

- Confusion has been created on use of fire extinguishers. This internal memo is to clarify the use of fire extinguishers.

- List of fire extinguishers and their usage

| Sl. No. | SKU | Description | Price including GST | Usage |
| --- | --- | --- | --- | --- |
|  | FIRE2009-Fire & Safety-Wet type Fire extinguisher--9-Ltr | Water type fire extinguisher also known wet type fire extinguisher. Standard capacity 9 ltrs. | Rs. 1,392 | This is the most commonly used fire extinguisher. Use in all internal spaces, staircases. Do not use near electrical installations. |
|  | FIRE7790-Fire & Safety-Dry type Fire extinguisher-ABC-6-Kgs. | ABC dry chemical powder fire extinguisher also known as dry type /ABC fire extinguisher. Standard capacity 6 kgs. | Rs.1,475 | This is to be used near all electrical installations like panel room, transformer, DG, lift machine room, HSD yard, HT yard, fire pump room, other electrical installations |
|  | FIRE6067-Fire & Safety-Dry type ABC Fire extinguisher-misc-Nos | ABC dry chemical powder fire extinguisher also known as dry type /ABC fire extinguisher. Standard capacity 25 kgs. | Rs.6,785 For 25Kg | One such fire extinguisher may be placed in the panel room or just outside the access to the panel room. |
|  | FIRE8857-Fire & Safety-Dry type Fire extinguisher-CO2-4.5-Kgs FIRE6733-Fire & Safety-Dry type Fire extinguisher-CO2-6-Kgs | CO2 type fire extinguisher. Standard capacity 4.5kgs. In some cases 6 kgs may be used | Rs.5,605 for4.5kgs Rs.11,682 for 6kgs | To be sparingly used. One or two extinguishers may be installed in critical areas like panel room, DG, HT yard, fire pump room. |

- Fire extinguishers:

  - Fire extinguishers are primarily of 3 types:

    - Dry type fire extinguisher – ABC – 6kgs – SKU FIRE7790- also referred to as powder type – use for electrical installation

    - Dry type fire extinguisher – CO2 – 4.5 or 6kgs – SKU FIRE6733 – rarely use.

    - Wet type fire extinguisher – 9ltrs – SKU FIRE 2009 – most often used.

  - Use wet type 9 ltrs fire extinguisher at most places. Use ABC/dry type fire extinguisher near electrical installations. CO2 fire extinguishers to be used only at select places – to be determined by MEP.

  - Guideline for usage /installation:

    - At transformer, each security kiosk, near generator, inside and outside panel room, outside lift machine room/top floor of machine room less lifts, ground floor of lift lobby – one ABC fire extinguisher to be installed. They may be installed at other places where electrical equipment are installed. Sites under construction – installation at security kiosk, electrical transformer and generator is mandatory.

    - In staircase landings – install one ABC/dry type fire extinguishers in each landing.

    - CO2 extinguishers may be sparingly used as per advice of MEP team.

    - Total no. of fire extinguishers must be more than or equal to the number provided in the approved fire plan.

    - These extinguishers must be fixed at a height of 4ft from FFL.

  - Along with fire extinguishers provide 3 nos fire buckets filled with sand on the stilt floor attached to a suitable stand.

Soham Modi.